AIDE-MEMOIRE (TENDER BRIEF)

Tender Name: EPC Package for Development of 1100 MW / 3300 MWh ISTS-Connected Battery Energy Storage System (BESS) at NTPC REL Khavda Solar Plant, Gujarat (Technical ... pp. 2, 7).
Bidding Reference: Bidding Document No: NGEL-CS-5779-004(BESS1)-9 (Technical ... p. 1).

🏛️ 1. Project Context & Business Model

- Stakeholder Framework: NTPC Green Energy Limited (NGEL), a subsidiary of NTPC Limited, is the employer (Technical ... p. 6). The project is developed for NTPC Renewable Energy Limited (NTPC REL), which is setting up 1200 MW of ISTS-connected Solar PV Projects at Khavda (Technical ... p. 7).

- Execution Philosophy: Single-Responsibility EPC Package mode spanning design, engineering, supply, erection, testing, commissioning, and associated performance warranties (Technical ... p. 7).

- Project Slicing (Four Blocks): The project is structured across four independent blocks, each handled through a distinct EPC package contract (Technical ... p. 7):

  - Block-1: 300 MW / 900 MWh at PSS-1 (Technical ... p. 7)

  - Block-2: 300 MW / 900 MWh at PSS-1 (Technical ... p. 7)

  - Block-3: 300 MW / 900 MWh at PSS-1 (Technical ... p. 7)

  - Block-4: 200 MW / 600 MWh at PSS-1 (Technical ... p. 7)

- Land Allocation: Land will be provided by the Owner on an "as-is, where-is" basis at an approximate density of 2.5 acres per 100 MWh (Technical ... p. 10).

🛠️ 2. Core Plant & Technical Specifications

- Total Project Rating: 1100 MW (AC deliverable) / 3300 MWh (AC deliverable) at the Point of Interconnection (POI) (Technical ... pp. 2, 8).

- Operating C-Rate: Set at 0.25 C (implied by 3-hour or 4-hour rated discharge systems at rated power) (Technical ... p. 26). The BESS must provide a minimum of 4 hours, 3 hours, or 2 hours of discharging capacity at rated power depending on the block configuration (Technical ... p. 26).

- Battery Technology: Advanced Chemistry Cells (ACCs) (Technical ... p. 10).

- Turnkey Asset Lifecycle: Sized for a minimum design lifecycle of 25 years from the date of final commissioning (accounting for progressive battery degradation over single daily cycle profiles) (Technical ... p. 40).

- Cyclic Endurance Floor: Offered battery units must be certified for a minimum lifespan of 10,000 operational cycles (Technical ... p. 40).

- Minimum Nameplate Initial Sizing: Bidders are strictly mandated to over-provision the initial nameplate capacity at COD to mitigate early degradation (Technical ... pp. 23, 41):

  - Blocks 1, 2, & 3 (900 MWh Deliverable): 990 MWh minimum installed nameplate capacity (Technical ... p. 41).

  - Block 4 (600 MWh Deliverable): 660 MWh minimum installed nameplate capacity (Technical ... p. 41).

- Mandatory Lifecycle Augmentation: Augmentation plans must include at least 15% of the awarded nameplate capacity spread proactively over the 15-year O&M tenure (Technical ... p. 27). Bidders must spread this capacity addition with at least 5% of the awarded capacity allocated in each 5-year block (Years 1–5, 6–10, and 11–15) (Technical ... p. 27).

🔌 3. Electrical Infrastructure & Power Evacuation

- Termination Point: Point of Coupling (POC) registers at the Owner's Indoor 33 kV Main Pooling Switchgear situated at the 400kV/33kV substation yard (Technical ... p. 8).

- Switchgear Extension Work: Contractors are fully responsible for physically extending both existing 33 kV bus sections of the respective 300 MW Solar Block switchgear (Technical ... pp. 38, 41). Bidders must mount one 33 kV, 3150 A evacuation feeder per bus section (total 2 feeders per BESS block) (Technical ... pp. 38, 41).

- Power Transformer Details: Each BESS block interfaces with one 315 MVA, 400 kV / 33 kV / 33 kV three-winding transformer featuring OLTC ±10% (Technical ... p. 9).

- Interconnection Point (POI): Final grid delivery point terminates at the 400 kV CTUIL Substation (KPS-3) via an existing 8 km twin AL-59 Moose transmission line (Technical ... p. 9).

- Sizing Loss Overheads: Sizing metrics must explicitly compensate for downstream equipment losses between the POC and POI: 1.0% Power Transformer losses and 0.25% Transmission Line losses (Technical ... p. 40).

- Auxiliary Power Sourcing: The entire BESS auxiliary supply framework must be tapped from metered 33 kV feeders on the BESS pooling switchgears built by the contractor (Technical ... p. 44). No external/additional pooling space or incoming feeders are provided inside the owner's switchgear (Technical ... pp. 42, 44).

📈 4. Performance Guarantees & Operational Window

- Round-Trip Efficiency (RTE): Bidders must guarantee a minimum monthly AC-to-AC Round-Trip Efficiency of 80%, calculated at the POC and explicitly inclusive of all plant auxiliary consumption and standby losses (Technical ... pp. 22-23).

- System Discharging Energy Availability: The asset must sustain a minimum of 98% annual energy availability during discharging windows over its complete operational life (Technical ... p. 24).

- Daily Dispatchable Energy Thresholds (MDn): Factoring in natural cell aging, the guaranteed dispatchable energy floor at the POI tracks as follows (Technical ... p. 23):

  - Year 1: 95% of the initially awarded capacity (Technical ... p. 23).

  - Years 2 through 15: 92% minimum guaranteed capacity (Technical ... p. 23).

  - Handover Gate: 92% deliverable capacity at the end of the 15-year O&M phase (Technical ... pp. 23, 29).

- Operational Schedulability Profile: Designed for 1 complete charge-discharge cycle per day (Technical ... p. 24). Owner can schedule full charging across a single or split stretch spanning up to 12 cumulative hours (Technical ... p. 26). Discharging can operate at full rated power for 2–4 hours or stretch across multiple sessions up to 8 cumulative hours at partial loads (Technical ... p. 26).

💰 5. Liquidated Damages (LD) During O&M

- RTE Underperformance Penalty: If the monthly measured AC-to-AC efficiency falls under the 80% specified target, the contractor faces penalties for excess charging energy calculated as (Technical ... p. 28):
\(\text{LD}_{\eta \text{Loss}}(\text{INR})=I\times C\times \left(\frac{1}{\eta _{\text{meas}}}-\frac{1}{0.80}\right)\times 10^{6}\)
(Where C is the total monthly actual discharging MUs at the POC, \(\eta _{\text{meas}}\) is the achieved monthly efficiency, and I is the fixed charging energy valuation set at ₹3.1 / kWh). (Technical ... pp. 22, 28)

- Discharging Availability Shortfall Penalty: Falling below the 98% annual discharging availability gateway incurs liquidated damages calculated as (Technical ... pp. 28-29):
\(\text{Liquidated\ Damages\ (INR)}=(0.98-Y^{\prime })\times B^{\prime }\times 1.25\times T\times 10^{6}\)
(Where Y' is the actual annual system availability during discharge, B' is the scheduled discharge energy for that specific year in MUs, and T is the fixed real-time market price ceiling set at ₹10 / kWh for the entire contract lifespan). (Technical ... p. 29)

- End-of-Life Handover Capacity Penalty: Failure to demonstrate the mandatory 92% capacity retention at the 15-year handover threshold triggers a long-range penalty scaled for a 5-year outlook (Technical ... p. 29):
\(\text{Liquidated\ Damages\ (INR)}=(0.92-Y^{\prime \prime })\times 1.25\times T\times P\times 365\times 1000\times 5\)
(Where Y'' is the actual verified percentage handover capacity, T = ₹10/kWh, and P is the designated project block capacity in MW). (Technical ... pp. 29-30)

- LD Financial Recovery Caps: O&M phase performance damages are deducted in the 4th quarter from the periodic O&M bills, capped strictly at a maximum of 25% of the Annual O&M Contract Value (Technical ... p. 30). Overages beyond this boundary are recovered by encashing lifecycle bank guarantees, which the contractor must replenish within three months (Technical ... p. 30).

- Absolute Asset Rejection Boundary: If the BESS fails to meet a baseline 50% of its stipulated availability during an O&M year for a cumulative period of 2 years or more, the entire BESS asset is liable for rejection under GCC guidelines (Technical ... p. 30).

🔒 6. Securities & Life Cycle Bank Guarantee (LCBG)

- O&M Phase Security Transition: While a standard Construction Performance Bank Guarantee (CPBG) operates until the end of the defect liability phase, contractors must transition to a dedicated Life Cycle Equipment Performance Bank Guarantee (LCBG) prior to CPBG release (Technical ... p. 32).

- LCBG Quantum: Valued at 8% of the main equipment cost (defined as the total contract price excluding O&M and Augmentation overheads) (Technical ... p. 32).

- Phased Release Modality: To ensure long-range accountability, the LCBG features a milestone relaxation cycle (Technical ... p. 33):

  - Initial Submission: 8% value filed post-successful PG test completion (Technical ... pp. 32-33).

  - Progressive Release: Each year from the 2nd year onwards, 4% of the LCBG value is released following successful compliance and performance parameters at the end of each operating year (Technical ... p. 33).

  - Final Release: Leftover remaining security balance is fully wound down at the end of the 15th project year following final handover clearance (Technical ... p. 33).

🌐 7. Grid Compliance & Simulation Criteria (Appendix-5)

- Model Submission Schedule: Contractors must submit comprehensive PSS/E (RMS level) and PSCAD (EMT level) simulation models along with a benchmarking report at least 12 months prior to the project's scheduled commissioning date (Technical ... pp. 13-14). Final validated models reflecting actual field tests must be updated within 1 month post-COD (Technical ... p. 15).

- Mathematical Error Tolerances: The deviation and error window between simulated model outputs and actual physical field test measurements during grid benchmarking exercises cannot exceed a maximum of 5% (Technical ... p. 37).

- Model Initialisation & Step Sizing: EMT models built in PSCAD must fully initialize within 3 seconds, have snapshot capability, and use a simulation time step of 10 μ s or greater during a standard 100-second flat run (Technical ... p. 37).

- Version Compatibility Boundaries: Simulation models must meet fixed engine compatibility rules (Technical ... p. 37):

  - EMT Platform: Fully compatible with PSCAD Version 4.6 and above, supporting Intel Visual Fortran 15 (or higher) and PSCAD V5 with GNU/Intel compilers (Technical ... p. 37).

  - RMS Platform: Fully compatible with PSS/E Version 34.4 and above, packaging all .sav, .dyr, .py, .idv, .sld, and .out structural configuration files (Technical ... p. 37).

- Power Quality & Fault Response Focus: Inverters (PCS) must demonstrate primary frequency control with adjustable droop settings, provide oscillation-free active/reactive power recovery during LVRT/HVRT events, and prioritize reactive power support according to voltage dips during faults (Technical ... pp. 12, 35). Bidders must measure and report harmonic contents, DC injection, and flicker parameters at least once a year throughout the entire 15-year O&M tenure (Technical ... pp. 15, 44).

1. Technical Elegibility Criteria

Bidders can typically qualify under one of three distinct routes, depending on whether they are grid-scale system integrators, standalone project developers, or executing via technology collaboration. [1]

- Route 1: Battery System Integration Experience

  - The bidder must have designed, supplied, erected/supervised erection, and successfully commissioned grid-connected Battery Energy Storage Systems (BESS) of a minimum cumulative capacity (often around 80 MWh to 100 MWh across multiple locations).

  - Out of these reference projects, at least one single-location BESS asset must have a minimum capacity of 20 MWh and must have been in successful operation for at least 6 months. [1]

- Route 2: Grid-Connected Renewable Energy (RE) Developer/EPC

  - Bidders who do not possess deep prior battery experience can qualify if they have executed large-scale infrastructure projects.

  - They must have designed, supplied, erected, and commissioned grid-connected Solar PV or Wind projects of a cumulative capacity of 100 MW or above.

  - At least one single-location anchor reference project must be of 40 MW or above and in successful operation for at least 6 months prior to the techno-commercial bid opening. [1, 2]

- Route 3: Sub-Station Evacuation Infrastructure Experience

  - The bidder must have executed at least one electrical pooling sub-station of 33 kV or above voltage level consisting of equipment like circuit breakers and power transformers as an EPC contractor or developer.

  - This sub-station must have been in successful operation for at least 1 year (or 6 months if in the RE sector). [1]

💰 2. Financial Qualification Criteria

The financial requirements ensure the bidder can support the intensive upfront capital expenditure (CapEx) cycle before milestone payments are unlocked. [1]

- Minimum Average Annual Turnover (MAAT): The bidder’s average annual turnover cannot be less than a specified financial threshold (typically calculated proportionally based on the estimated project block value) during any three financial years out of the preceding five financial years. [1]

- Net Worth Guardrail: The financial net worth of the bidder as on the last day of the preceding financial year must be positive and not less than 100% of their paid-up share capital. Holding company net worth line support can be leveraged via formal board resolution extensions. [1, 2]

- Liquid Assets Buffer: Bidders must demonstrate active credit lines, immediate cash balances, or liquid asset availability of a designated value to prove stable daily operational cash flow capability during construction. [1]

🌐 3. Statutory, OEM & Geopolitical Compliance (Critical Blocks)

- Geopolitical Cross-Border Restrictions (ToT Rule): In line with Ministry of Finance guidelines, any bidder or consortium partner possessing a Transfer of Technology (ToT) arrangement with an entity from a country sharing a land border with India is eligible only if registered with the Competent Registration Authority. [1]

- Lithium-Ion Waiver: Notably, the Ministry of Power provides an active waiver on this specific cross-border registration requirement exclusively for bidders utilizing Lithium-Ion cell technologies. [1]

- Battery OEM Track Record: The proposed sub-vendor/OEM for the battery banks must have a proven technological history—specifically having manufactured and supplied at least 50 MWh of stationary battery systems globally over the last 3 years. [1]

- EMS Indigenous Code Compliance: To protect the national power grid from cyber security threats, the application layer software for the Energy Management System (EMS) must be developed indigenously within India (Technical ... p. 3).